## Step Response PID Tuning
Process Parameters |  | Bump Test
Process Gain [Kp] | 1
Process Time Const. [tau] | 10
Process Dead Time [td] | 1
Ziegler - Nichols | Kc | Ti | Td | ITAE [Load] | Kc | Ti | Td
P | 10 |  |  | PI | 8.1469 | 3.0998
PI | 9 | 3.3 |  | PID | 12.011 | 2.1711 | 0.38541
PID | 12 | 2 | 0.5
Cohen - Coon | Kc | Ti | Td | ITAE [Setpoint] | Kc | Ti | Td
P | 10.3333 |  |  | PI | 4.8294 | 9.8668
PI | 9.3333 | 2.7545 |  | PID | 6.9108 | 12.7992 | 0.3627
PID | 13.5833 | 2.3623 | 0.35714
MIGO | Kc | Ti | Td | AMIGO | Kc | Ti | Td
PI [Integrating] | 3.5 | 13.4 |  | PID [Integrating] | 4.5 | 8 | 0.5
PI | 2.8236 | 6.0769 |  | PID | 4.7 | 4.2 | 0.48544
lambda [λ] | 10
tau Ratio | 1
Lambda Tuning | Kc | Ti | Td
PΙ [Integrating] | 0.17355 | 21
PI | 0.90909 | 10
closed loop time const | 10
tau Ratio | 1
IMC Tuning | Kc | Ti | Td
P [Integrating] | 0.1
PI | 0.90909 | 10
PID | 1 | 10.5 | 0.47619
Note on A17: M-constrained Integral Gain Optimization
Note on A18: Gain = (dPV/dt)/dCO
Note on A21: = [Closed Loop tau] > 3 * td
Note on A22: = [Closed Loop tau] / [Open Loop tau] ratio > 3 : Very stable 3 > ratio > 2 : Normal design 2 > ratio > 1 : Fast design
Note on A24: Gain = (dPV/dt)/dCO
Note on A27: = [Closed Loop tau] > 3 * td
Note on A28: = [Closed Loop tau] / [Open Loop tau] ratio > 3 : Very stable 3 > ratio > 2 : Normal design 2 > ratio > 1 : Fast design
Note on A30: Gain = (dPV/dt)/dCO
Note on F7: Integral of Time-weighted Absolute Error
Note on F12: Integral of Time-weighted Absolute Error
Note on F17: Approximate MIGO
Note on F18: Gain = (dPV/dt)/dCO

## Freq Response PID Tuning
Process Parameters
Kcu | 8.3
Pu | 7.9
Ziegler - Nichols | Kc | Ti | Td
P | 4.15
PI | 3.7765 | 6.5807
PID (25% overshoot) | 4.98 | 3.95 | 0.9875
PID (small overshoot) | 2.739 | 3.95 | 2.6307
PID (no overshoot) | 1.66 | 3.95 | 2.6307
Note on A3: Kcu = GM [Gain Margin]
Note on A4: Pu = 2π / ω