## License Agreement
SunSpec Alliance
SunSpec Infomation Model Reference
Date Generated: 2016-04-20
This document is generated programatically from the canonical model definitions contained in the SunSpec model repository.
For the most up-to-date version of this document, go to: www.sunspec.org/download
Copyright SunSpec Alliance 2009-2015. All Rights Reserved.
This document and the information contained herein is provided on an "AS IS" basis and the SunSpec Alliance DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the SunSpec Technical Committee and as governed by the SunSpec IPR Policy. The complete policy of the SunSpec Alliance can be found at www.sunspec.org.
Prepared by the SunSpec Alliance
4030 Moorpark Avenue, Suite 109
San Jose, CA 95117
Website: www.sunspec.org
Email: info@sunspec.org

## Summary
Summary
This spreadsheet describes SunSpec Alliance Data Models and Modbus maps.
Each spreadsheet tab describes an individual data model of one of the following types:
Id Range | Model Type
1 | Common
2 | Aggregator
010 to 019 | Network Configuration
100 series | Inverter
200 series | Meter
300 series | Environmental
400 series | String Combiner
500 series | Panel
600 series | Tracker
700 series | Reserved by SunSpec Alliance
800 series | Storage
900 - 63000 | Reserved by SunSpec Alliance
64000 series | Vendor Specific
This document includes data models that are of Approved, Test, and Draft status.
Before using any of these models, please check the release status of the model in question.
Only Approved models may be SunSpec Certified.
Canonical Representation
The documentation contained in this spreadsheet is derived from SunSpec Model Definition XML (SMDX) files, which can be downloaded from www.sunspec.org/modelreference/
Please note that the SMDX files are the canonical (definitive) representations of SunSpec models.
SunSpec Specification Documentation
All current SunSpec specifications (PDF format) are available for free downloading at http://sunspec.org/download/.
SunSpec Certification
If you would like to have your product SunSpec Certified, please read the information available at http://sunspec.org/sunspec-certified-program/
and then email certification@sunspec.org to schedule your test.

## Index
Model | Label | Description | Notes
1 | Common | All SunSpec compliant devices must include this as the first model
2 | Basic Aggregator | Aggregates a collection of models for a given model id
3 | Secure Dataset Read Request | Request a digial signature over a specifed set of data registers | Used in conjunction witgh Secure Dataset Read Response Model
4 | Secure Dataset Read Response | Compute a digial signature over a specifed set of data registers
5 | Secure Write Request | Include a digial signature along with the control data
6 | Secure Write Sequential Request | Include a digial signature along with the control data
7 | Secure Write Response Model (DRAFT 1) | Include a digital signature over the response | Used in conjunction with a Secure Write Request
8 | Get Device Security Certificate | Security model for PKI
9 | Set Operator Security Certificate | Security model for PKI
10 | Communication Interface Header | To be included first for a complete interface description
11 | Ethernet Link Layer | Include to support a wired ethernet port
12 | IPv4 | Include to support an IPv4 protocol stack on this interface
13 | IPv6 | Include to support an IPv6 protocol stack on this interface
14 | Proxy Server | Include this block to allow for a proxy server
15 | Interface Counters Model | Interface counters
16 | Simple IP Network | Include this model for a simple IPv4 network stack
17 | Serial Interface | Include this model for serial interface configuration support
18 | Cellular Link | Include this model to support a cellular interface link
19 | PPP Link | Include this model to configure a Point-to-Point Protocol link
101 | Inverter (Single Phase) | Include this model for single phase inverter monitoring
102 | Inverter (Split-Phase) | Include this model for split phase inverter monitoring
103 | Inverter (Three Phase) | Include this model for three phase inverter monitoring
111 | Inverter (Single Phase) FLOAT | Include this model for single phase inverter monitoring using float values
112 | Inverter (Split Phase) FLOAT | Include this model for split phase inverter monitoring using float values
113 | Inverter (Three Phase) FLOAT | Include this model for three phase inverter monitoring using float values
120 | Nameplate | Inverter Controls Nameplate Ratings | Ref 3: 8.14.3.2, Ref 4: 17
121 | Basic Settings | Inverter Controls Basic Settings | Ref 3: 8.4.2.1, Ref 4: 17
122 | Measurements_Status | Inverter Controls Extended Measurements and Status | Ref 3: 8.14.3.2, Ref 4: 17
123 | Immediate Controls | Immediate Inverter Controls | Ref 3: 8.7.1.2, 8.7.2.2, 8.7.3.2
124 | Storage | Basic Storage Controls | Ref 3: 8.7.4.2
125 | Pricing | Pricing Signal | Ref 3: 8.7.5.1; Ref 4: 6
126 | Static Volt-VAR | Static Volt-VAR Arrays | Ref 3: 8.8.1.2
127 | Freq-Watt Param | Parameterized Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
128 | Dynamic Reactive Current | Dynamic Reactive Current | Ref 3: 8.10.1.2; Ref 4: 12
129 | LVRTD | LVRT Must Disconnect | Ref 4: 11
130 | HVRTD | HVRT Must Disconnect | Ref 4: 11
131 | Watt-PF | Watt-Power Factor | Ref 3: 8.11.1.2
132 | Volt-Watt | Volt-Watt | Ref 3: 8.12.1.2
133 | Basic Scheduling | Basic Scheduling | Ref 2: 2.2.8
134 | Freq-Watt Crv | Curve-Based Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
135 | LFRT | Low Frequency Ride-through | Ref 4: 11
136 | HFRT | High Frequency Ride-through | Ref 4: 11
137 | LVRTC | LVRT must remain connected | Ref 4: 11
138 | HVRTC | HVRT must remain connected | Ref 4: 11
160 | Multiple MPPT Inverter Extension Model
201 | Meter (Single Phase)single phase (AN or AB) meter | Include this model for single phase (AN or AB) metering
202 | split single phase (ABN) meter
203 | wye-connect three phase (abcn) meter
204 | delta-connect three phase (abc) meter
211 | single phase (AN or AB) meter |  | Float
212 | split single phase (ABN) meter |  | Float
213 | wye-connect three phase (abcn) meter |  | Float
214 | delta-connect three phase (abc) meter |  | Float
220 | Secure AC Meter Selected Readings | Include this model for secure metering
302 | Irradiance Model | Include to support various irradiance measurements
303 | Back of Module Temperature Model | Include to support variable number of back of module temperature measurements
304 | Inclinometer Model | Include to support orienation measurements
305 | GPS | Include to support location measurements
306 | Reference Point Model | Include to support a standard reference point
307 | Base Met | Base Meteorolgical Model | This model supersedes model 301
308 | Mini Met Model | Include to support a few basic measurements
401 | String Combiner (Current) | A basic string combiner | This model is SUPERSEDED by model 403
402 | String Combiner (Advanced) | An advanced string combiner | This model is SUPERSEDED by model 404
403 | String Combiner (Current) | A basic string combiner model | This model supersedes model 401
404 | String Combiner (Advanced) | An advanced string combiner including voltage and energy measurements | This model supersedes model 402
501 | Solar Module | A solar module model supporing DC-DC converter | Float
502 | Solar Module | A solar module model supporing DC-DC converter | Integer
601 | Tracker Controller DRAFT 2 | Monitors and controls multiple trackers | Trackers may include GPS model 305 for location information
801 | Energy Storage Base Model
802 | Battery Base Model
803 | Lithium-Ion Battery Model
63001 | SunSpec Test Model 1
63002 | SunSpec Test Model 2
64001 | Veris Status and Configuration
64020 | Mersen GreenString
64101 | Eltek Inverter Extension
64110 | OutBack AXS device
64111 | Basic Charge Controller
64112 | OutBack FM Charge Controller

## 1
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes | Modbus Address | get | set
Header |  | 0 |  | 1 | ID | Common | 1 | uint16 |  |  | R | M | All SunSpec compliant devices must include this as the first model |  | 2
Header |  | 1 |  | 1 | L |  | 66 | uint16 |  |  | R | M | Model Length |  | 3
4
Fixed Block |  | 2 | 0 | 16 | Mn | Manufacturer |  | string |  |  | R | M | Well known value registered with SunSpec for compliance |  | 4
Fixed Block |  | 18 | 16 | 16 | Md | Model |  | string |  |  | R | M | Manufacturer specific value (32 chars) |  | 20
Fixed Block |  | 34 | 32 | 8 | Opt | Options |  | string |  |  | R | O | Manufacturer specific value (16 chars) |  | 36
Fixed Block |  | 42 | 40 | 8 | Vr | Version |  | string |  |  | R | O | Manufacturer specific value (16 chars) |  | 44
Fixed Block |  | 50 | 48 | 16 | SN | Serial Number |  | string |  |  | R | M | Manufacturer specific value (32 chars) |  | 52
Fixed Block |  | 66 | 64 | 1 | DA | Device Address |  | uint16 |  |  | RW | O | Modbus device address |  | 68 | sunspecInterface.model1.DA = modbusHandlerGetSlaveAddress(); | modbusHandlerSetSlaveAddress(sunspecInterface.model1.DA);
Fixed Block |  | 67 | 65 | Size: 1; Name: Pad; Type: pad; R/W: R | O | Force even alignment |  | 69

## 17
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes | Modbus Address | get | set
Header |  | 0 |  | 1 | ID | Serial Interface | 17 | uint16 |  |  | R | M | Include this model for serial interface configuration support |  | 70
Header |  | 1 |  | 1 | L |  | 12 | uint16 |  |  | R | M | Model Length |  | 71
72
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name (8 chars) |  | 72 | size_t i; UartName name = modbusHandlerGetName(); for(i=0; i<LENGTHOF(name.s); i++) { sunspecInterface.model17.Nam[i] = name.s[i]; } | size_t i; UartName name; for(i=0; i<LENGTHOF(name.s); i++) { name.s[i] = sunspecInterface.model17.Nam[i]; } modbusHandlerSetName(name);
Fixed Block |  | 6 | 4 | 2 | Rte | Rate |  | uint32 | bps |  | RW | M | Interface baud rate in bits per second |  | 76 | uint32_t bps = uartGetBpsFromEnumeration(modbusHandlerGetBaudRate()); sunspecUint32ToSSU32(&sunspecInterface.model17.Rte, bps); | int32_t bps = (int32_t)sunspecSSU32ToUint32(&sunspecInterface.model17.Rte); modbusHandlerSetBaudRate(uartGetBaudEnumeration(bps));
Fixed Block |  | 8 | 6 | 1 | Bits | Bits |  | uint16 |  |  | RW | M | Number of data bits per character |  | 78 | UartProtocol protocol = modbusHandlerGetProtocol(); if(protocol == UART_RTU_N82) sunspecInterface.model17.Bits = 2; else sunspecInterface.model17.Bits = 1;
Fixed Block |  | 9 | 7 | 1 | Pty | Parity |  | enum16 |  |  | RW | M | Bitmask value. Parity setting |  | 79 | UartProtocol protocol = modbusHandlerGetProtocol(); if(protocol == UART_RTU_E81) sunspecInterface.model17.Pty = SUNSPECMODEL17_PTY_EVEN; else if(protocol == UART_RTU_O81) sunspecInterface.model17.Pty = SUNSPECMODEL17_PTY_ODD; else sunspecInterface.model17.Pty = SUNSPECMODEL17_PTY_NONE;
Fixed Block |  | 10 | 8 | 1 | Dup | Duplex |  | enum16 |  |  | RW | O | Enumerated value. Duplex mode | Fixed at ‘Half.’ | 80
Fixed Block |  | 11 | 9 | 1 | Flw | Flow Control |  | enum16 |  |  | RW | O | Flow Control Method | Fixed at ‘No flow control.’ | 81
Fixed Block |  | 12 | 10 | 1 | Typ | Interface Type |  | enum16 |  |  | R | O | Enumerated value. Interface type | Fixed at ‘RS485’ | 82
Fixed Block |  | 13 | 11 | 1 | Pcol | Protocol |  | enum16 |  |  | R | O | Enumerated value. Serial protocol selection | Fixed at ‘Modbus’ | 83
enum16 | Pty |  |  | Name: NONE; Label: none; Value: 0 |  | No Parity
enum16 | Pty |  |  | Name: ODD; Label: odd; Value: 1 |  | Odd Parity
enum16 | Pty |  |  | Name: EVEN; Label: even; Value: 2 |  | Even Parity
enum16 | Dup |  |  | Name: FULL; Label: full; Value: 0 |  | Full Duplex
enum16 | Dup |  |  | Name: HALF; Label: half; Value: 1 |  | Half Duplex
enum16 | Flw |  |  | Name: NONE; Label: none; Value: 0 |  | No flow control
enum16 | Flw |  |  | Name: HW; Label: hardware; Value: 1 |  | Hardware flow control
enum16 | Flw |  |  | Name: XONXOFF; Label: software; Value: 2 |  | Soft (XON/XOFF) flow control
enum16 | Typ |  |  | Name: UNKNOWN; Label: unknown; Value: 0 |  | Unknown interface type
enum16 | Typ |  |  | Name: RS232; Label: RS232; Value: 1 |  | RS232 interface type
enum16 | Typ |  |  | Name: RS485; Label: RS485; Value: 2 |  | RS485 interface type
enum16 | Pcol |  |  | Name: UNKNOWN; Label: unknown; Value: 0 |  | Unknown protocol
enum16 | Pcol |  |  | Name: MODBUS; Label: Modbus; Value: 1 |  | Modbus protocol
enum16 | Pcol |  |  | Name: VENDOR; Label: vendor specific; Value: 2

## 103
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes | Modbus Address | get | set
Header |  | 0 |  | 1 | ID | Inverter (Three Phase) | 103 | uint16 |  |  | R | M | Include this model for three phase inverter monitoring |  | 84
Header |  | 1 |  | 1 | L |  | 50 | uint16 |  |  | R | M | Model Length |  | 85
86
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | uint16 | A | A_SF | R | M | AC Current | Sum of active phases | 86 | sunspecInterface.model103.A = (int16_t) myround(PCC_getAcMonitorGridCurrentRms_SI(0U, PCC_ACM_APPARENT));
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | uint16 | A | A_SF | R | M | Phase A Current | Connected Phase | 87 | sunspecInterface.model103.AphA = (uint16_t)myround(PCC_getAcMonitorGridCurrentRms_SI(1U, PCC_ACM_APPARENT));
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | uint16 | A | A_SF | R | M | Phase B Current | Connected Phase | 88 | sunspecInterface.model103.AphB = (uint16_t)myround(PCC_getAcMonitorGridCurrentRms_SI(2U, PCC_ACM_APPARENT));
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | uint16 | A | A_SF | R | M | Phase C Current | Connected Phase | 89 | sunspecInterface.model103.AphC = (uint16_t)myround(PCC_getAcMonitorGridCurrentRms_SI(3U, PCC_ACM_APPARENT));
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M |  |  | 90
Fixed Block |  | 7 | 5 | 1 | PPVphAB | Phase Voltage AB |  | uint16 | V | V_SF | R | O | Phase Voltage AB |  | 91 | sunspecInterface.model103.PPVphAB = (uint16_t)myround(PCC_getAcMonitorGridVoltageRms_SI(1U, CMM_AC_NETWORK_LOCAL, PCC_ACM_APPARENT, PCC_ACM_LINE) * 10.0f);
Fixed Block |  | 8 | 6 | 1 | PPVphBC | Phase Voltage BC |  | uint16 | V | V_SF | R | O | Phase Voltage BC |  | 92 | sunspecInterface.model103.PPVphBC = (uint16_t)myround(PCC_getAcMonitorGridVoltageRms_SI(2U, CMM_AC_NETWORK_LOCAL, PCC_ACM_APPARENT, PCC_ACM_LINE) * 10.0f);
Fixed Block |  | 9 | 7 | 1 | PPVphCA | Phase Voltage CA |  | uint16 | V | V_SF | R | O | Phase Voltage CA |  | 93 | sunspecInterface.model103.PPVphCA = (uint16_t)myround(PCC_getAcMonitorGridVoltageRms_SI(3U, CMM_AC_NETWORK_LOCAL, PCC_ACM_APPARENT, PCC_ACM_LINE) * 10.0f);
Fixed Block |  | 10 | 8 | 1 | PhVphA | Phase Voltage AN |  | uint16 | V | V_SF | R | M | Phase Voltage AN |  | 94 | sunspecInterface.model103.PhVphA = (uint16_t)myround(PCC_getAcMonitorGridVoltageRms_SI(1U, CMM_AC_NETWORK_LOCAL, PCC_ACM_APPARENT, PCC_ACM_PHASE) * 10.0f);
Fixed Block |  | 11 | 9 | 1 | PhVphB | Phase Voltage BN |  | uint16 | V | V_SF | R | M | Phase Voltage BN |  | 95 | sunspecInterface.model103.PhVphB = (uint16_t)myround(PCC_getAcMonitorGridVoltageRms_SI(2U, CMM_AC_NETWORK_LOCAL, PCC_ACM_APPARENT, PCC_ACM_PHASE) * 10.0f);
Fixed Block |  | 12 | 10 | 1 | PhVphC | Phase Voltage CN |  | uint16 | V | V_SF | R | M | Phase Voltage CN |  | 96 | sunspecInterface.model103.PhVphC = (uint16_t)myround(PCC_getAcMonitorGridVoltageRms_SI(3U, CMM_AC_NETWORK_LOCAL, PCC_ACM_APPARENT, PCC_ACM_PHASE) * 10.0f);
Fixed Block |  | 13 | 11 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M |  |  | 97
Fixed Block |  | 14 | 12 | 1 | W | Watts |  | int16 | W | W_SF | R | M | AC Power |  | 98 | sunspecInterface.model103.W = (int16_t) myround(sunspecScale(PCC_getAcMonitorGridPowerRms_SI(0U, PCC_ACM_REAL), sunspecInterface.model103.W_SF));
Fixed Block |  | 15 | 13 | Size: 1; Name: W_SF; Type: sunssf; R/W: RW | M |  |  | 99
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | uint16 | Hz | Hz_SF | R | M | Line Frequency |  | 100 | sunspecInterface.model103.Hz = (uint16_t)myround(PCC_getAcMonitorFrequencyHz_SI(0U, CMM_AC_NETWORK_LOCAL) * 10.0f); /// \todo copied from canInterface.c
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | M |  |  | 101
Fixed Block |  | 18 | 16 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power |  | 102 | sunspecInterface.model103.VA = (int16_t) myround(sunspecScale(PCC_getAcMonitorGridPowerRms_SI(0U, PCC_ACM_APPARENT), sunspecInterface.model103.VA_SF));
Fixed Block |  | 19 | 17 | Size: 1; Name: VA_SF; Type: sunssf; R/W: RW | O |  |  | 103
Fixed Block |  | 20 | 18 | 1 | VAr | VAr |  | int16 | VAr | VAr_SF | R | O | AC Reactive Power |  | 104 | sunspecInterface.model103.VAr = (int16_t) myround(sunspecScale(PCC_getAcMonitorGridPowerRms_SI(0U, PCC_ACM_REACTIVE), sunspecInterface.model103.VAr_SF));
Fixed Block |  | 21 | 19 | Size: 1; Name: VAr_SF; Type: sunssf; R/W: RW | O |  |  | 105
Fixed Block |  | 22 | 20 | 1 | PF | PF |  | int16 |  | PF_SF | R | O | AC Power Factor |  | 106 | sunspecInterface.model103.PF = (int16_t) myround(sunspecScale(PCC_getAcMonitorGridCosPhi_SI(0U), sunspecInterface.model103.PF_SF));
Fixed Block |  | 23 | 21 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O |  |  | 107
Fixed Block |  | 24 | 22 | 2 | WH | WattHours |  | acc32 | Wh | WH_SF | R | M | AC Energy |  | 108
Fixed Block |  | 26 | 24 | Size: 1; Name: WH_SF; Type: sunssf; R/W: R | M |  |  | 110
Fixed Block |  | 27 | 25 | 1 | DCA | DC Amps |  | uint16 | A | DCA_SF | R | O | DC Current |  | 111 | sunspecInterface.model103.DCA = (uint16_t)myround(PCC_getDcMonitorDcCurrent_SI());
Fixed Block |  | 28 | 26 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | O |  |  | 112
Fixed Block |  | 29 | 27 | 1 | DCV | DC Voltage |  | uint16 | V | DCV_SF | R | O | DC Voltage |  | 113 | sunspecInterface.model103.DCV = (uint16_t)myround(PCC_getDcMonitorDcVoltage_SI());
Fixed Block |  | 30 | 28 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O |  |  | 114
Fixed Block |  | 31 | 29 | 1 | DCW | DC Watts |  | int16 | W | DCW_SF | R | O | DC Power |  | 115 | //sunspecInterface.model103.DCW = (int16_t)myround(sunspecScale(myround(_IQtoF(PDC_filt.Out)*PU_DCPOWER), sunspecInterface.model103.DCW_SF));
Fixed Block |  | 32 | 30 | Size: 1; Name: DCW_SF; Type: sunssf; R/W: RW | O |  |  | 116
Fixed Block |  | 33 | 31 | 1 | TmpCab | Cabinet Temperature |  | int16 | C | Tmp_SF | R | M | Cabinet Temperature | Module internal ambient temperature. | 117 | sunspecInterface.model103.TmpCab = (int16_t)myround(_IQ22toF(MESD_Measurements.aux.temp.meas.tInternal)*10.0f);
Fixed Block |  | 34 | 32 | 1 | TmpSnk | Heat Sink Temperature |  | int16 | C | Tmp_SF | R | O | Heat Sink Temperature |  | 118 | sunspecInterface.model103.TmpSnk = (int16_t)myround(_IQ22toF(MESD_Measurements.aux.temp.comp.tInverter)*10.0f); /// \todo CAMPed from canInterface
Fixed Block |  | 35 | 33 | 1 | TmpTrns | Transformer Temperature |  | int16 | C | Tmp_SF | R | O | Transformer Temperature | Not implemented | 119
Fixed Block |  | 36 | 34 | 1 | TmpOt | Other Temperature |  | int16 | C | Tmp_SF | R | O | Other Temperature | Not implemented | 120
Fixed Block |  | 37 | 35 | Size: 1; Name: Tmp_SF; Type: sunssf; R/W: R | M |  |  | 121
Fixed Block |  | 38 | 36 | 1 | St | Operating State |  | enum16 |  |  | R | M | Not implemented. Use StVnd |  | 122
Fixed Block |  | 39 | 37 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code |  | 123 | sunspecInterface.model103.StVnd = (SunspecModel103_StVnd)getStateNumber();
Fixed Block |  | 40 | 38 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields |  | 124 | sunspecInterface.model103.Evt1.DC_OVER_VOLT = faultStat.flags.DCOvervoltage; sunspecInterface.model103.Evt1.MANUAL_SHUTDOWN = faultStat.flags.EStopShutdown; sunspecInterface.model103.Evt1.OVER_TEMP = faultStat.flags.IGBTOvertemp; sunspecInterface.model103.Evt1.MEMORY_LOSS = faultStat.flags.InvalidEEHeader ¦¦ faultStat.flags.InvalidEESection ¦¦ faultStat.flags.SchedulerBGTask ¦¦ faultStat.flags.StackOverflow; sunspecInterface.model103.Evt1.HW_TEST_FAILURE = faultStat.flags.ControlHardwareFail;
Fixed Block |  | 42 | 40 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use |  | 126
Fixed Block |  | 44 | 42 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events |  | 128 | sunspecInterface.model103.EvtVnd1.HARDWARE_ENABLE = supervisorGetHardwareEnable(); sunspecInterface.model103.EvtVnd1.AC_PWR_AVAIL = gridMonitor_isNetworkUsable(CMM_AC_NETWORK_LOCAL); sunspecInterface.model103.EvtVnd1.DC_PWR_AVAIL = !faultStat.flags.DCUndervoltage; sunspecInterface.model103.EvtVnd1.PWR_CRCT_EN = (PWMD_getControlGroupGenState(CMM_CONTROL_GROUP_CNT, 0U) == PWMD_GENERATION_ACTIVE); sunspecInterface.model103.EvtVnd1.MX1 = relayIsClosed(relayMX1); sunspecInterface.model103.EvtVnd1.MX2 = relayIsClosed(relayMX2); sunspecInterface.model103.EvtVnd1.K1 = relayIsClosed(relayK1); sunspecInterface.model103.EvtVnd1.K2 = relayIsClosed(relayK2); sunspecInterface.model103.EvtVnd1.CTL_MSG_VALID = systemGetMasterAlive(); sunspecInterface.model103.EvtVnd1.PWR_CMD_VALID = referenceHandler_getPwrCmdValid(); sunspecInterface.model103.EvtVnd1.CUR_CMD_VALID = referenceHandler_getCurCmdValid(); sunspecInterface.model103.EvtVnd1.DC_CMD_VALID = referenceHandler_getDcCmdValid(); sunspecInterface.model103.EvtVnd1.PH_ROTAT_STAT = (PCD_getPhaseSequenceDetect(CMM_AC_NETWORK_LOCAL) == PCD_PHASE_SEQUENCE_POSITIVE); sunspecInterface.model103.EvtVnd1.LV_DETECTED = gridMonitor_isNetworkLive(CMM_AC_NETWORK_LOCAL); sunspecInterface.model103.EvtVnd1.REM_AC_AVAIL = false; sunspecInterface.model103.EvtVnd1.REM_PH_ROTAT_STAT = false; sunspecInterface.model103.EvtVnd1.REM_LV_DETECTED = false; sunspecInterface.model103.EvtVnd1.DI1_STAT = digitalInputRead(&digins[0]); sunspecInterface.model103.EvtVnd1.DI2_STAT = digitalInputRead(&digins[1]); sunspecInterface.model103.EvtVnd1.DI3_STAT = digitalInputRead(&digins[2]); sunspecInterface.model103.EvtVnd1.DI4_STAT = digitalInputRead(&digins[3]); sunspecInterface.model103.EvtVnd1.DO1_STAT = digitalOutputRead(&digouts[0]); sunspecInterface.model103.EvtVnd1.DO2_STAT = digitalOutputRead(&digouts[1]); sunspecInterface.model103.EvtVnd1.DO3_STAT = digitalOutputRead(&digouts[2]); sunspecInterface.model103.EvtVnd1.DO4_STAT = digitalOutputRead(&digouts[3]);
Fixed Block |  | 46 | 44 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events | Not implemented | 130
Fixed Block |  | 48 | 46 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events | Not implemented | 132
Fixed Block |  | 50 | 48 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events | Not implemented | 134
enum16 | St |  |  | Name: OFF; Label: Off; Value: 1 |  | Device is not operating
enum16 | St |  |  | Name: SLEEPING; Label: Sleeping; Value: 2 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Name: STARTING; Label: Starting; Value: 3 |  | Device is staring up
enum16 | St |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: THROTTLED; Label: Throttled; Value: 5 |  | Device is operating at reduced power output
enum16 | St |  |  | Name: SHUTTING_DOWN; Label: Shutting down; Value: 6 |  | Device is shutting down
enum16 | St |  |  | Name: FAULT; Label: Fault; Value: 7 |  | One or more faults exist
enum16 | St |  |  | Name: STANDBY; Label: Standby; Value: 8 |  | Device is in standby mode
enum16 | StVnd |  |  | Name: POR; Label: por; Value: 0 |  | Power On Reset
enum16 | StVnd |  |  | Name: READY; Label: Ready; Value: 1 |  | Device is in standby mode
enum16 | StVnd |  |  | Name: FOLLOWING; Label: Following; Value: 2 |  | Device is running in grid following mode
enum16 | StVnd |  |  | Name: FAULT; Label: Fault; Value: 3 |  | One or more faults exist
enum16 | StVnd |  |  | Name: FORMING; Label: Forming; Value: 4 |  | Device is running in grid forming mode
enum16 | StVnd |  |  | Name: RECONNECT_DELAY; Label: Reconnect Delay; Value: 5 |  | Grid available, but Device is waiting for reconnect delay to expire
enum16 | StVnd |  |  | Name: AREA_EPS_LOST; Label: Area EPS Loss; Value: 7 |  | Disconnected from grid due to abnormal grid condition(s)
enum16 | StVnd |  |  | Name: CHARGE; Label: Charging DC; Value: 8 |  | Charging DC link. AC side operating as a passive rectifier
enum16 | StVnd |  |  | Name: RIDETHRU; Label: Ride Through; Value: 9 |  | High/Low Voltage or Frequency ride-through condition active
enum16 | StVnd |  |  | Name: CESSATION; Label: Momentary Cessation; Value: 10 |  | Momentary power cessation active due to high/low grid frequency or voltage
enum16 | StVnd |  |  | Name: TRANS; Label: Transitioning; Value: 11 |  | Transitioning between forming/following modes
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid shutdown; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15
bitfield32 | EvtVnd1 |  |  | Name: HARDWARE_ENABLE; Label: Hardware enable status; Value: 0 |  | Status of the hardware enable.
bitfield32 | EvtVnd1 |  |  | Name: AC_PWR_AVAIL; Label: AC Power Available; Value: 1 |  | Indicates that AC power is connected and that voltage and frequency are within nominal ranges.
bitfield32 | EvtVnd1 |  |  | Name: DC_PWR_AVAIL; Label: DC Power Available; Value: 2 |  | Indicates that DC bus voltage is within operating range.
bitfield32 | EvtVnd1 |  |  | Name: PWR_CRCT_EN; Label: Power Circuit Enabled; Value: 3 |  | Indicates whether the switching devices are active.
bitfield32 | EvtVnd1 |  |  | Name: MX1; Label: MX1 relay status; Value: 4 |  | MX1 relay status
bitfield32 | EvtVnd1 |  |  | Name: MX2; Label: MX2 relay status; Value: 5 |  | MX2 relay status
bitfield32 | EvtVnd1 |  |  | Name: K1; Label: Precharge status; Value: 6 |  | K1 precharge relay status.
bitfield32 | EvtVnd1 |  |  | Name: K2; Label: K2 Relay status; Value: 7 |  | K2 DC Run relay status.
bitfield32 | EvtVnd1 |  |  | Name: CTL_MSG_VALID; Label: Control commands valid; Value: 8 |  | Indicates the validity of the control bits. Message must be received within the serial timeout and parameter data within range to be considered valid.
bitfield32 | EvtVnd1 |  |  | Name: PWR_CMD_VALID; Label: Power command Valid; Value: 9 |  | Indicates the validity of the real and reactive power commands.
bitfield32 | EvtVnd1 |  |  | Name: CUR_CMD_VALID; Label: Current command Valid; Value: 10 |  | Indicates the validity of the real and reactive current commands
bitfield32 | EvtVnd1 |  |  | Name: PH_ROTAT_STAT; Label: Phase rotation status; Value: 11 |  | Phase rotation order. When L1 phase angle leads L2 phase angle, rotation is considered positive.
bitfield32 | EvtVnd1 |  |  | Name: LV_DETECTED; Label: Line voltage detected; Value: 12 |  | Flag indicating if voltage is detected on L1, L2 or L3.
bitfield32 | EvtVnd1 |  |  | Name: RSVD; Label: Unused; Value: 13 |  | Unused
bitfield32 | EvtVnd1 |  |  | Name: REM_AC_AVAIL; Label: Remote AC Power Available; Value: 14 |  | Indicates that remote AC power is connected and that voltage and frequency are within nominal ranges.
bitfield32 | EvtVnd1 |  |  | Name: REM_PH_ROTAT_STAT; Label: Remote phase rotation status; Value: 15 |  | Remote phase rotation order. When L1 phase angle leads L2 phase angle, rotation is considered positive.
bitfield32 | EvtVnd1 |  |  | Name: REM_LV_DETECTED; Label: Remote Line Voltage Detected; Value: 16 |  | Flag indicating if voltage is detected on remote L1, L2 or L3.
bitfield32 | EvtVnd1 |  |  | Name: DI1_STAT; Label: DI1 Status; Value: 17 |  | Status of digital input 1
bitfield32 | EvtVnd1 |  |  | Name: DI2_STAT; Label: DI2 Status; Value: 18 |  | Status of digital input 2
bitfield32 | EvtVnd1 |  |  | Name: DI3_STAT; Label: DI3 Status; Value: 19 |  | Status of digital input 3
bitfield32 | EvtVnd1 |  |  | Name: DI4_STAT; Label: DI4 Status; Value: 20 |  | Status of digital input 4
bitfield32 | EvtVnd1 |  |  | Name: DO1_STAT; Label: DO1 Status; Value: 21 |  | Status of digital output 1
bitfield32 | EvtVnd1 |  |  | Name: DO2_STAT; Label: DO2 Status; Value: 22 |  | Status of digital output 2
bitfield32 | EvtVnd1 |  |  | Name: DO3_STAT; Label: DO3 Status; Value: 23 |  | Status of digital output 3
bitfield32 | EvtVnd1 |  |  | Name: DO4_STAT; Label: DO4 Status; Value: 24 |  | Status of digital output 4
bitfield32 | EvtVnd1 |  |  | Name: DC_CMD_VALID; Label: DC link reference commands Valid; Value: 25 |  | Indicates the validity of the DC Bus reference commands.

## 65534
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes | Modbus Address | get | set
Header |  | 0 |  | 1 | ID | EPC_Control | 65534 | uint16 |  |  | R | M |  |  | 136
Header |  | 1 |  | 1 | L |  | 44 | uint16 |  |  | R | M | Model Length |  | 137
138
Fixed Block |  | 2 | 0 | 2 | CmdBits | Control Bits |  | bitfield32 |  |  | RW | O | Operational command flags | Message required at a rate of at least once per second in all states. | 138 |  | bool forceRelayCmds[relayListLength]; systemClearFaults(sunspecInterface.model65534.CmdBits.FltClr); if (sunspecInterface.model65534.CmdBits.FltClr) { resetPumpFaults(&pumpDrive); } if (sunspecInterface.model65534.CmdBits.WrnClr) { WARNING_CLEARALL(); } //SyncToRemote = sunspecInterface.model65534.CmdBits.RemoteSync; fanSetSpeedOverride(&fanCoolant, sunspecInterface.model65534.CmdBits.ForceFan, 100); supervisorSetHwEnableLogic(sunspecInterface.model65534.CmdBits.InvertHwEnable); afeParams->cfgFlags.enableUPSMode = sunspecInterface.model65534.CmdBits.EnableUps; if (sunspecInterface.model65534.CmdBits.EnableSplitPhase == 1) { PCD_setPresetDisplacementRequest(PCD_PHASE_DISPLACEMENT_180); } else { PCD_setPresetDisplacementRequest(PCD_PHASE_DISPLACEMENT_120); } if (sunspecInterface.model65534.CmdBits.PhaseRotation == 1) { PCD_setPhaseSequenceRequest(PCD_PHASE_SEQUENCE_POSITIVE); } else { PCD_setPhaseSequenceRequest(PCD_PHASE_SEQUENCE_NEGATIVE); } forceRelayCmds[relayMX1] = sunspecInterface.model65534.CmdBits.ForceMX1; forceRelayCmds[relayMX2] = sunspecInterface.model65534.CmdBits.ForceMX2; forceRelayCmds[relayK1] = sunspecInterface.model65534.CmdBits.ForceK1 ; forceRelayCmds[relayK2] = sunspecInterface.model65534.CmdBits.ForceK2 ; afeHandleRelayCmds(&forceRelayCmds);
Fixed Block |  | 4 | 2 | 2 | CmdRealPwr | Real Power Command |  | int32 | W | PWR_SF | RW | O | Commanded real power (W) while in grid following mode - positive real power is defined as power being put into the ac network. |  | 140 |  | if(systemIsModbusControlActive() && pqCommandsValid()) { referenceHandler_setP(sunspecSSS32ToInt32(&sunspecInterface.model65534.CmdRealPwr)); }
Fixed Block |  | 6 | 4 | 2 | CmdReactivePwr | Reactive Power Command |  | int32 | VAr | PWR_SF | RW | O | Commanded reactive power (VA) while in grid following mode - positive reactive power is defined as the converter having a leading power factor. |  | 142 |  | if(systemIsModbusControlActive() && pqCommandsValid()) { referenceHandler_setQ(sunspecSSS32ToInt32(&sunspecInterface.model65534.CmdReactivePwr)); }
Fixed Block |  | 8 | 6 | Size: 1; Name: PWR_SF; Type: sunssf; R/W: R | O |  |  | 144
Fixed Block |  | 9 | 7 | 1 | CmdV | Voltage Command |  | uint16 | V | V_SF | RW | O | Desired output voltage while in grid forming mode. |  | 145 |  | referenceHandler_setVCmd(sunspecInterface.model65534.CmdV*0.1f);
Fixed Block |  | 10 | 8 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | O |  |  | 146
Fixed Block |  | 11 | 9 | 1 | CmdHz | Frequency Command |  | uint16 | Hz | HZ_SF | RW | O | Desired output frequency while in grid forming mode. |  | 147 |  | (void)PPC_setCommonConfigNominalFrequency((float)sunspecInterface.model65534.CmdHz * 0.1f);
Fixed Block |  | 12 | 10 | Size: 1; Name: HZ_SF; Type: sunssf; R/W: R | O |  |  | 148
Fixed Block |  | 13 | 11 | 1 | CtlSrc | Control Source |  | enum16 |  |  | RW | O | Master control source for the inverter |  | 149 | if (systemIsModbusControlActive()) { sunspecInterface.model65534.CtlSrc = SUNSPECMODEL65534_CTLSRC_Modbus; } else { sunspecInterface.model65534.CtlSrc = SUNSPECMODEL65534_CTLSRC_CAN; } | if (sunspecInterface.model65534.CtlSrc == SUNSPECMODEL65534_CTLSRC_Modbus) { systemSetModbusControlActive(); } else { systemSetCanControlActive(); }
Fixed Block |  | 14 | 12 | 1 | IMPPT | MPPT Current |  | int16 | A | A_SF | R | O | Measured MPPT current (Hydra Solar inverter only) |  | 150 | #ifdef HYDRA sunspecInterface.model65534.IMPPT = (int16_t)myround(_IQtoF(DCDC_getControlSourceTotalCurrentRef(DCDC_CTRL_SRC_MPPT, true)) * PU_Iline); #endif
Fixed Block |  | 15 | 13 | 1 | Ivctl | Volt. Ref Current |  | int16 | A | A_SF | R | O | Measured Voltage-controlled current (Hydra inverter only) |  | 151 | #ifdef HYDRA sunspecInterface.model65534.Ivctl = (int16_t)myround(_IQtoF(DCDC_getControlSourceTotalCurrentRef(DCDC_CTRL_SRC_VOLTAGE, true)) * PU_Iline); #endif
Fixed Block |  | 16 | 14 | 1 | Vsol | Solar Voltage |  | int16 | V | V_SF | R | O | Measured solar input voltage (Hydra Solar inverter only) |  | 152 | #ifdef HYDRA sunspecInterface.model65534.Vsol = (int16_t)myround(_IQtoF(-remoteLineVoltages[LV_FBK_SOL]) * PU_Vline_Rem); #endif
Fixed Block |  | 17 | 15 | 1 | Vbat | Battery Voltage |  | int16 | V | V_SF | R | O | Measured battery input voltage (Hydra inverter only) |  | 153 | #ifdef HYDRA sunspecInterface.model65534.Vbat = (int16_t)myround(_IQtoF( remoteLineVoltages[LV_FBK_BAT]) * PU_Vline_Rem); #endif
Fixed Block |  | 18 | 16 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | O |  |  | 154
Fixed Block |  | 19 | 17 | 2 | Spcl | Special operations |  | bitfield32 |  |  | RW | O | Special operation command flags |  | 155 |  | static bool writingEE = false; if((sunspecInterface.model65534.Spcl.Save)&&(!writingEE)) { writingEE = true; eeHandlerSave(false); //store to NV } else { if(!sunspecInterface.model65534.Spcl.Save) { writingEE = false; } }
Fixed Block |  | 21 | 19 | 1 | SysFlt | System Fault Code |  | uint16 |  |  | R | O | Fault code (if non-0, indicates that 1 or more system faults is active) |  | 157 | sunspecInterface.model65534.SysFlt = faultStat.flags.ControlHardwareFail; sunspecInterface.model65534.SysFlt += faultStat.flags.SchedulerBGTask << 1; sunspecInterface.model65534.SysFlt += faultStat.flags.EEUninitialized << 2; sunspecInterface.model65534.SysFlt += faultStat.flags.StackOverflow << 3; sunspecInterface.model65534.SysFlt += faultStat.flags.InsufficientHeap << 4; sunspecInterface.model65534.SysFlt += faultStat.flags.PWMISROverrun << 5; sunspecInterface.model65534.SysFlt += faultStat.flags.SchedulerTaskInit << 6; sunspecInterface.model65534.SysFlt += faultStat.flags.msISROverrun << 7; sunspecInterface.model65534.SysFlt += faultStat.flags.tenMsISROverrun << 8;
Fixed Block |  | 22 | 20 | 2 | FltFlgs | Fault Flags |  | bitfield32 |  |  | R | O | Fault status |  | 158 | sunspecInterface.model65534.FltFlgs.Estp = faultStat.flags.EStopShutdown; sunspecInterface.model65534.FltFlgs.ACOC = faultStat.flags.ACOvercurrent; sunspecInterface.model65534.FltFlgs.DCOC = faultStat.flags.DCOvercurrent; sunspecInterface.model65534.FltFlgs.DCOV = faultStat.flags.DCOvervoltage; sunspecInterface.model65534.FltFlgs.PDOT = faultStat.flags.IGBTOvertemp; sunspecInterface.model65534.FltFlgs.IOT = faultStat.flags.InverterOvertemp; sunspecInterface.model65534.FltFlgs.CmdMsg = faultStat.flags.LossOfValidCmd; sunspecInterface.model65534.FltFlgs.DCUV = faultStat.flags.DCUndervoltage; sunspecInterface.model65534.FltFlgs.GrdLss = faultStat.flags.LossOfAC; sunspecInterface.model65534.FltFlgs.Trans = faultStat.flags.IllegalTransition; sunspecInterface.model65534.FltFlgs.EEH = faultStat.flags.InvalidEEHeader; sunspecInterface.model65534.FltFlgs.EES = faultStat.flags.InvalidEESection; sunspecInterface.model65534.FltFlgs.Cool = faultStat.flags.CoolingSystemFail; sunspecInterface.model65534.FltFlgs.TOLAC = faultStat.flags.TimedACOverload; sunspecInterface.model65534.FltFlgs.TOLDC = faultStat.flags.TimedDCOverload; sunspecInterface.model65534.FltFlgs.SIO = faultStat.flags.SIOTimeout; sunspecInterface.model65534.FltFlgs.CtlBd = faultStat.flags.CtlBdVoltage; sunspecInterface.model65534.FltFlgs.Iimblnc = faultStat.flags.IlegImbalance; sunspecInterface.model65534.FltFlgs.DiDt = faultStat.flags.Didt; sunspecInterface.model65534.FltFlgs.Flw = faultStat.flags.LowCoolingFlow; sunspecInterface.model65534.FltFlgs.POR = faultStat.flags.PORTimeout; sunspecInterface.model65534.FltFlgs.Thrm = faultHandlerIsCfgdFaultActive(FLT_CFG_THERMAL_OVERLOAD); sunspecInterface.model65534.FltFlgs.Fan = faultHandlerIsCfgdFaultActive(FLT_CFG_FAN_CIRCUIT);
Fixed Block |  | 24 | 22 | 2 | WrnFlgs | Warning Flags |  | bitfield32 |  |  | R | O | Warning status |  | 160 | sunspecInterface.model65534.WrnFlgs.CANW = warningStat.flags.CANWarning; sunspecInterface.model65534.WrnFlgs.CANEP = warningStat.flags.CANErrorPassive; sunspecInterface.model65534.WrnFlgs.Thrm = faultHandlerIsCfgdWarningActive(FLT_CFG_THERMAL_OVERLOAD); sunspecInterface.model65534.WrnFlgs.Fan = faultHandlerIsCfgdWarningActive(FLT_CFG_FAN_CIRCUIT);
Fixed Block |  | 26 | 24 | 1 | CmdRealCurrent | Real Current Command |  | int16 | A | A_SF | RW | O | Commanded real current (A) while in grid following mode - positive real power is defined as power being put into the ac network. |  | 162 |  | if(systemIsModbusControlActive()) { referenceHandler_setId(sunspecInterface.model65534.CmdRealCurrent); }
Fixed Block |  | 27 | 25 | 1 | CmdReactiveCurrent | Reactive Current Command |  | int16 | A | A_SF | RW | O | Commanded reactive current (A) while in grid following mode - positive reactive power is defined as the converter having a leading power factor. |  | 163 |  | if(systemIsModbusControlActive()) { referenceHandler_setIq(sunspecInterface.model65534.CmdReactiveCurrent); }
Fixed Block |  | 28 | 26 | 1 | RealCurrent | Measured Real Current |  | int16 | A | A_SF | R | O | Measured real current |  | 164 | sunspecInterface.model65534.RealCurrent = (int16_t)myround(PCC_getAcMonitorGridCurrentRms_SI(0U, PCC_ACM_REAL));
Fixed Block |  | 29 | 27 | 1 | ReactiveCurrent | Measured Reactive Current |  | int16 | A | A_SF | R | O | Measured reactive current |  | 165 | sunspecInterface.model65534.ReactiveCurrent = (int16_t)myround(PCC_getAcMonitorGridCurrentRms_SI(0U, PCC_ACM_REACTIVE));
Fixed Block |  | 30 | 28 | 1 | LocVAC | Local Grid VAC |  | uint16 | V | V_SF | R | O | AC Voltage of local grid |  | 166 | sunspecInterface.model65534.LocVAC = (int16_t)myround(PCC_getAcMonitorGridVoltageRms_SI(0U, CMM_AC_NETWORK_LOCAL, PCC_ACM_APPARENT, PCC_ACM_LINE) * 10.0f);
Fixed Block |  | 31 | 29 | 1 | RemPhVphA | Remote Phase Voltage AN |  | uint16 | V | V_SF | R | O | Remote Phase Voltage AN |  | 167 | //RemPhVphA = (uint16_t)myround(_IQtoF(ieee1547_getLineToNeutralVoltage(&ieee1547LVM, IEEE1547_VLINEA))* PU_VlineRMS * 10.0f);
Fixed Block |  | 32 | 30 | 1 | RemPhVphB | Remote Phase Voltage BN |  | uint16 | V | V_SF | R | O | Remote Phase Voltage BN |  | 168 | //RemPhVphB = (uint16_t)myround(_IQtoF(ieee1547_getLineToNeutralVoltage(&ieee1547LVM, IEEE1547_VLINEB))* PU_VlineRMS * 10.0f);
Fixed Block |  | 33 | 31 | 1 | RemPhVphC | Remote Phase Voltage CN |  | uint16 | V | V_SF | R | O | Remote Phase Voltage CN |  | 169 | //RemPhVphC = (uint16_t)myround(_IQtoF(ieee1547_getLineToNeutralVoltage(&ieee1547LVM, IEEE1547_VLINEC))* PU_VineRMS * 10.0f);
Fixed Block |  | 34 | 32 | 1 | RemVAC | Remote Grid VAC |  | uint16 | V | V_SF | R | O | AC Voltage of remote grid |  | 170 | //sunspecInterface.model65534.RemVAC = (int16_t)myround(_IQtoF(vAcRemote_filt.Out)*PU_Vline*10.0f);
Fixed Block |  | 35 | 33 | 1 | RemHz | Hz |  | uint16 | Hz | HZ_SF | R | O | Remote grid Line Frequency |  | 171 | //sunspecInterface.model65534.RemHz = (int16_t)myround(pll_getFrequency(&pll_remote)*10.0f);
Fixed Block |  | 36 | 34 | Size: 1; Name: TMP_SF; Type: sunssf; R/W: R | O |  |  | 172
Fixed Block |  | 37 | 35 | 1 | TmpInt | Internal Temp |  | int16 | C | TMP_SF | R | O | Internal ambient temperature |  | 173 | sunspecInterface.model65534.TmpInt = (int16_t)myround(_IQ22toF(MESD_Measurements.aux.temp.meas.tInternal)*10.0f);
Fixed Block |  | 38 | 36 | 1 | TmpInlet | Inlet Temp |  | int16 | C | TMP_SF | R | O | Coolant inlet temperature |  | 174 | #ifdef AIRCOOLED_HEATSINK sunspecInterface.model65534.TmpInlet = (int16_t)myround(_IQ22toF(MESD_Measurements.aux.temp.comp.tInv)*10.0f); //max IGBT temp #else sunspecInterface.model65534.TmpInlet = (int16_t)myround(_IQ22toF(MESD_Measurements.aux.temp.meas.tInlet)*10.0f); #endif
Fixed Block |  | 39 | 37 | 1 | RemPPVphCA | Remote Phase Voltage CA |  | uint16 | V | V_SF | R | O | Remote Phase Voltage CA |  | 175 | //RemPPVphCA = (uint16_t)myround(_IQtoF(ieee1547_getLineToLineVoltage (&ieee1547LVM, IEEE1547_VLINEA))* PU_VlineRMS * 10.0f);
Fixed Block |  | 40 | 38 | 1 | RemPPVphAB | Remote Phase Voltage AB |  | uint16 | V | V_SF | R | O | Remote Phase Voltage AB |  | 176 | //RemPPVphAB = (uint16_t)myround(_IQtoF(ieee1547_getLineToLineVoltage (&ieee1547LVM, IEEE1547_VLINEB))* PU_VlineRMS * 10.0f);
Fixed Block |  | 41 | 39 | 1 | RemPPVphBC | Remote Phase Voltage BC |  | uint16 | V | V_SF | R | O | Remote Phase Voltage BC |  | 177 | //RemPPVphBC = (uint16_t)myround(_IQtoF(ieee1547_getLineToLineVoltage (&ieee1547LVM, IEEE1547_VLINEC))* PU_VlineRMS * 10.0f);
Fixed Block |  | 42 | 40 | 1 | DcILim | DC Current Limit |  | uint16 | A | A_SF | RW | O | DC Link Current Limit |  | 178 |  | if(systemIsModbusControlActive()) { referenceHandler_setIdcLim(sunspecInterface.model65534.DcILim); }
Fixed Block |  | 43 | 41 | 1 | DcVLim | DC Voltage Limit |  | uint16 | V | V_SF | RW | O | DC Link Voltage Limit |  | 179 |  | if(systemIsModbusControlActive()) { referenceHandler_setVdcLim(sunspecInterface.model65534.DcVLim*0.1f); }
Fixed Block |  | 44 | 42 | 1 | LineILim | Line Current Limit |  | uint16 | A | A_SF | RW | O | Line Current Limit |  | 180 |  | if(systemIsModbusControlActive()) { referenceHandler_setIlineLim(sunspecInterface.model65534.LineILim); }
Fixed Block |  | 45 | 43 | 1 | InputCurrent | Input Current Reference |  | int16 | A | A_SF | RW | O | Input current reference (Hydra inverter only) |  | 181 |  | if(systemIsModbusControlActive()) { referenceHandler_setInputCurrent(sunspecInterface.model65534.InputCurrent); }
bitfield32 | CmdBits |  |  | Name: En; Label: Enable; Value: 0 |  | Run command. When set to a value of 'Enable', causes transition to grid forming or grid following mode depending on whether AC power is detected. Must be set to 'Disable' to leave POR or FAULTED state.
bitfield32 | CmdBits |  |  | Name: FltClr; Label: Fault Clear; Value: 1 |  | Clears latched fault status.
bitfield32 | CmdBits |  |  | Name: VsenseRem; Label: Use Voltage Sense as Remote; Value: 2 |  | Use voltage sense input as either local or remote reference.
bitfield32 | CmdBits |  |  | Name: RemoteSync; Label: Sync to Remote Source; Value: 3 |  | Sync and connect to remote source.
bitfield32 | CmdBits |  |  | Name: ForceMX1; Label: Close MX1; Value: 4 |  | If set to 'Force On,' will force the relay closed, overriding firmware state machine commands. Meant for diagnostic purposes only.
bitfield32 | CmdBits |  |  | Name: ForceMX2; Label: Close MX2; Value: 5 |  | If set to 'Force On,' will force the relay closed, overriding firmware state machine commands. Meant for diagnostic purposes only.
bitfield32 | CmdBits |  |  | Name: ForceK1; Label: Close K1; Value: 6 |  | If set to 'Force On,' will force the relay closed, overriding firmware state machine commands. Meant for diagnostic purposes only.
bitfield32 | CmdBits |  |  | Name: ForceK2; Label: Close K2; Value: 7 |  | If set to 'Force On,' will force the relay closed, overriding firmware state machine commands. Meant for diagnostic purposes only.
bitfield32 | CmdBits |  |  | Name: ForceFan; Label: Force Fan On; Value: 8 |  | Forces cooling fan on (air cooled units only)
bitfield32 | CmdBits |  |  | Name: InvertHwEnable; Label: Invert Hardware Enable; Value: 9 |  | Inverts the logic of the Hardware Enable input.
bitfield32 | CmdBits |  |  | Name: EnableUps; Label: Enable UPS Mode; Value: 10 |  | Enables uninterruptible operation when transitioning from GRID FOLLOWING to GRID FORMING operation. If operating in GRID FOLLOWING mode, and AC grid voltage is interrupted, the module will transition to GRID FORMING mode, with no interruption in power.
bitfield32 | CmdBits |  |  | Name: EnableSplitPhase; Label: Enable Split Phase Mode; Value: 11 |  | Dictates to the module whether it is connected to a three-phase (four wire) or split phase (L1, L2 and N) electrical system.
bitfield32 | CmdBits |  |  | Name: PhaseRotation; Label: Phase Rotation Direction; Value: 12 |  | Specifies phase rotation direction. Only active while transitioning from READY to GRID_FORMING.
bitfield32 | CmdBits |  |  | Name: WrnClr; Label: Warning Clear; Value: 13 |  | Clears latched warning status.
enum16 | CtlSrc |  |  | Name: CAN; Label: CAN control; Value: 0 |  | CAN is the primary control source, though Modbus monitoring is still active
enum16 | CtlSrc |  |  | Name: Modbus; Label: Modbus control; Value: 1 |  | Modbus is the primary control source, though CAN communication is still active.
bitfield32 | Spcl |  |  | Name: Save; Label: Save NV; Value: 0 |  | Store non-volatile parameters to memory (present settings will persist power cycle.
bitfield32 | FltFlgs |  |  | Name: Estp; Label: E-Stop shutdown; Value: 0 |  | The emergency-stop input was activated.
bitfield32 | FltFlgs |  |  | Name: ACOC; Label: AC Overcurrent; Value: 1 |  | AC Overcurrent
bitfield32 | FltFlgs |  |  | Name: DCOC; Label: DC Overcurrent; Value: 2 |  | DC Overcurrent
bitfield32 | FltFlgs |  |  | Name: DCOV; Label: DC Overvoltage; Value: 3 |  | DC Overvoltage
bitfield32 | FltFlgs |  |  | Name: PDOT; Label: Device Overtemp; Value: 4 |  | Power device overtemperature
bitfield32 | FltFlgs |  |  | Name: IOT; Label: Inverter Overtemp; Value: 5 |  | Inverter overtemperature
bitfield32 | FltFlgs |  |  | Name: CmdMsg; Label: Invalid command message; Value: 6 |  | Loss of valid command message
bitfield32 | FltFlgs |  |  | Name: DCUV; Label: DC Undervoltage; Value: 7 |  | DC Undervoltage
bitfield32 | FltFlgs |  |  | Name: GrdLss; Label: Grid Loss; Value: 8 |  | Loss of AC grid
bitfield32 | FltFlgs |  |  | Name: Trans; Label: Illegal transition; Value: 9 |  | Illegal state transition requested by master
bitfield32 | FltFlgs |  |  | Name: EEH; Label: Bad EE header; Value: 10 |  | Invalid EEPROM header
bitfield32 | FltFlgs |  |  | Name: EES; Label: Bad EE section; Value: 11 |  | Invalid EEPROM section
bitfield32 | FltFlgs |  |  | Name: Cool; Label: Cooling system; Value: 12 |  | Cooling system failure
bitfield32 | FltFlgs |  |  | Name: TOLAC; Label: AC Timed overload; Value: 13 |  | AC timed overload trip
bitfield32 | FltFlgs |  |  | Name: TOLDC; Label: DC Timed overload; Value: 14 |  | DC timed overload trip
bitfield32 | FltFlgs |  |  | Name: SIO; Label: Serial timeout; Value: 15 |  | Serial interface timeout
bitfield32 | FltFlgs |  |  | Name: CtlBd; Label: Control Board Voltage; Value: 16 |  | Control board voltage
bitfield32 | FltFlgs |  |  | Name: Iimblnc; Label: Leg Imbalance; Value: 17 |  | Current leg imbalance
bitfield32 | FltFlgs |  |  | Name: DiDt; Label: Current rise; Value: 18 |  | Rapid rise in output current
bitfield32 | FltFlgs |  |  | Name: Flw; Label: Cooling Flow; Value: 19 |  | Low cooling flow
bitfield32 | FltFlgs |  |  | Name: Thrm; Label: Thermal Overload; Value: 20 |  | Thermal Overload Input
bitfield32 | FltFlgs |  |  | Name: Fan; Label: Fan Circuit; Value: 21 |  | Fan Circuit
bitfield32 | FltFlgs |  |  | Name: POR; Label: POR Timeout; Value: 22 |  | Power on reset state timeout
bitfield32 | WrnFlgs |  |  | Name: CANW; Label: CAN Warning; Value: 0 |  | CAN Warning
bitfield32 | WrnFlgs |  |  | Name: CANEP; Label: CAN Error Passive; Value: 1 |  | CAN Error Passive
bitfield32 | WrnFlgs |  |  | Name: Thrm; Label: Thermal Overload; Value: 2 |  | Thermal Overload Input
bitfield32 | WrnFlgs |  |  | Name: Fan; Label: Fan Circuit; Value: 3 |  | Fan Circuit